## Sheet1
ETHERNET CAT 6A DISTRIBUTION
OFFICE SPACES | 6 GENERAL OFFICE SPACES | OFFICE DIRECTOR | FRONT OFFICE MANAGER | OFFICE MANAGER | CONFERENCE ROOM | KITCHEN ROOM | NETWORK/ELECTRICAL RACK | HALL | TOTAL
CAT6A UNDERGROUND PORTS | 4 x 8 JUNCTION IP PORTS | 1 x 5 JUNCTION IP PORT | 1 x 5 JUNCTION IP PORT | 1 x 5 JUNCTION IP PORT | 1 x 5 JUNCTION IP PORT | 2 x 5 JUNCTION IP PORTS | N/A | N/A | 10
CAT6A CEILING PORTS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2 X 2 JUNCTION IP PORTS | 2
PVC CONDUITS | 1 PVC CONDUIT = 3/4 " PVC SCHEDULE 40 CONDUIT, AREA = 0.824" > 2 x STANDARD CAT6A OUTER DIAMETER - 0.240" x 2, OUTER DIAMETER / INNER DIAMETER = 2 x 0.240" / 0.824" < 50%, 1 PVC CONDUIT = 1 CAT6A PAIR FOR MAXIMUM CLEARANCE
POWER DISTRIBUTION
OFFICE SPACES | 6 GENERAL OFFICE SPACES | OFFICE DIRECTOR | FRONT OFFICE MANAGER | OFFICE MANAGER | CONFERENCE ROOM | KITCHEN ROOM | NETWORK/ELECTRICAL RACK | HALL | TOTAL
OFFICE ROOMS | 1 DUAL RESPECTACLE CONTACTS / DESK X 4 DESKS -> 4 CONTACTS X 3 FAR LEFT OFFICES -> 12 CONTACTS + 8 CONTACTS (CENTER ROOM) -> 20 DUAL CONTACTS + 2 DUAL CONTACTS -> 22 DUAL CONTACTS | 4 DUAL CONTACTS | 4 DUAL CONTACTS | 4 DUAL CONTACTS | 9 DUAL CONTACTS | 3 DUAL CONTACTS + 3 DUAL CONTACTS | N/A | N/A | 49
SYSTEM | SYSTEM VOLTAGE - (220V - 240V), CALCULATIONS - 230 V
CONTROL ROOM
CALCULATIONS | I = 2 kW / 230 V = 8.69 A -> STANDARD CIRCUIT BREAKER TYPE B RATED 15 A MCB -> 12 AWG STANDARD WIRING MAX 15 A - 20 A -> 1/2" SCHEDULE 40 PVC CONDUIT / 1 PAIR 12 AWG WIRING -> OUTER DIAMETER / INNER PVC DIAMETER -> 2 x 0.08"/ 0.622" < 30% -> 1 PVC CONDUIT = 1 PAIR 12 AWG WIRE
OFFICES
CALCULATIONS | ENTIRE OFFICE SPACE -> 22 X 300 W (PC/MONITORS) + 9 X 150 W (MEETING ROOM LAPTOPS/ETC) + 5 X 400W (LARGER WORKSTATIONS) + 1000W (IT/NETWORK) = 10.95kW < ≈ 3 x (230 V X 20 A, mimimum power supplied to a room)
CALCULATIONS | 12 AWG CABLE RATED 20 A -> 1/2" SCHEDULE 40 PVC = 1 PAIR 12 AWG -> STANDARD CIRCUIT BREAKER TYPE B RATED 15 A MCB
HALL
CALCULATIONS | FOR LIGHTING APPLICATIONS -> P < = (1.20 design factor) x (230 V x 15 A) -> 14 AWG CABLE RATED 15 A -> 12 x 0.0097 in^2/0.294 in^2 < 40% -> 1/2" SCHEDULE 40 PVC = 12 x AWG 14 WIRES -> STANDARD CIRCUIT BREAKER TYPE B RATED 15 A MCB
KITCHEN
CALCULATIONS | FOR POWER HUNGRY APPLIANCES -> P < = (1.20 design factor) x (230 V x 30 A) -> 10 AWG CABLE RATED 30 A -> 5 x 0.021 in^2/0.294 in^2 < 40% -> 1/2" SCHEDULE 40 PVC = 5 x AWG 14 WIRES -> STANDARD CIRCUIT BREAKER TYPE B RATED 30 A MCB FOR MAXIMUM CLEARANCE
HVAC
1 X GMV-280WL/C-X | I = 7.78kW/230V = 33.83 A -> 1.25 X 33.83 A = 42.23 A -> 1 X 8 AWG CABLE RATED 40 A - 50 A -> 1 X CIRCUIT BREAKER DOUBLE POLE TYPE B 50 A MCB -> 1/2" SCHEDULE 40 PVC = 1 x AWG 8 WIRE
3 X GMVND45T/E-T | I = 45 W/230V = 0.20 A -> 3 X 14 AWG CABLE RATED 12 A - 15 A -> 1 X STANDARD CIRCUIT BREAKER TYPE B RATED 15 A MCB -> 1/2" SCHEDULE 40 PVC = 3 x AWG 14 WIRES
1 X GMVND36T/E-T, 1 X GMVND28T/E-T, 3 X GMVND22T/E-T | I = 30 W/230V = 0.13 A -> 5 X 14 AWG CABLE RATED 12 A - 15 A -> 1 X STANDARD CIRCUIT BREAKER TYPE B RATED 15 A MCB -> 1/2" SCHEDULE 40 PVC = 5 x AWG 14 WIRES
1 X CHRU-TF | I = 690W/230V = 3 A -> 1.25 X 3 A = 3.75 A -> 1 X 12 AWG CABLE RATED 15 A - 20 A -> 1 X STANDARD CIRCUIT BREAKER TYPE B RATED 15 A MCB -> 1/2" SCHEDULE 40 PVC = 1 x AWG 12 WIRES
1 X ф250 HEATER | I = 6kW/230V = 26.09 A -> 1.25 X 26.09 A = 32.61 A -> 1 X 8 AWG CABLE RATED 40 A - 50 A -> 1 X CIRCUIT BREAKER DOUBLE POLE TYPE B 50 A MCB -> 1/2" SCHEDULE 40 PVC = 1 x AWG 8 WIRE
NYY O/J CABLE TO AWG CABLE CONVERSION
EXPLANATION | Since original drawing uses NYY O/J cables and design uses AWG cables, junction and distribution boxes are used in drawing to represent this conversion
CALCULATIONS | Example: Input - 1 NYY O/J 3 x 16mm^2 -> Junction box with Pe = 20 kW -> Pe, in = Pe, out ≈ 7 x 2.5mm^2 12 AWG cables with circuit breakers attached just before the junction box to protect both wiring and hardware. See wiring diagram for clearer view